## Basic PPM Spec.
Specification for Basic Prepayement Energy Meter
S/N | PARAMETER | TECHNICAL REQUIREMENT
1. | Nominal Voltage | 1Ø-230V,1-ph,2-wire system, 3Ø-230V/400V,3-ph,4-wire system for use in balanced and unbalanced load conditions
2. | Operating Voltage | -40% to +10%
3. | Current Rating | 5(60)A, 3x5(100)A
4. | Frequency | 50±2%Hz
5. | Accuracy Class | 1
6. | Encryption Algorithm | Standard Transfer Specification (STS)
7. | Operating Temperature | Up to 60oC
8. | Storage Temperature | Up to 70oC
9. | Relative Humidity | 95% at 45oC non-condensing
10. | Maximum KWH credit stored | 99,999.9 KWh(1Ø),999,999.9KWh(3Ø)
11. | Credit transfer number | 20 Digits encryption
12. | Protection | High resistance to short circuit
13. | Impulse Withstand Voltage | Preferably greater than 6KV
14. | Insulation Withstand Voltage | 2KV per minute
15. | Name plate | a. Indelible serial number shall not be less than eleven (11) digits and legibly printed
b. Size of the digit of the meter serial number shall be a minimum of 5mm x 3mm
c. Bar code shall be printed below the meter serial number
d. Manufacturers name and trademark
e. Place of manufacture
f. Year of manufacture
g. Reference Voltage, Current and Frequency
h. Class Index
i. Meter Constant
j. Owner/Utility’s Identity
16. | Front Panel Indication/Display | Include but not limited to the following:
a. Three level credit LED display
b. Green-when energy stored is full
c. Yellow-when remaining credit will last for 3- days. The red flashes when the remaining energy will last for 11/2 days.
d. Blue-Consumption rate indicator
e. LCD credit status display
f. Credit transfer number accept/reject
g. Tamper
17. | Special Mode Display for | Display up to 3 parameters according to programming to be specified:
| Engineering/Management | a) Normal display –LCD
i. Duplicate copy of token inserted
ii. Credit Dispensing Unit identification number and KWh (or voucher serial number) inserted.
iii. Electricity Dispenser (ED) full of units.
iv. No power ON ED
v. No credit on ED
vi. Credit rejects or accepts.
vii. Remaining Credit.
viii. Instantaneous Power
ix. Total KWh used in the past 24 hrs.
x. Total KWh used in the past 30 days.
xi. Historical value minimum of 6months KWh
xii. Total KWh used since the ED was installed.
b) Display only available with valid codes.
c) Display only available within chosen programming or engineering mode.
For the purpose of these specifications, items b) and c) above are treated as one. These shall be accessible only to utility staff.
a. Over current trip level.
b. Green-Yellow Light emitting diode (LED) display change over level in KWh (high).
c. Yellow-Red LED display change over level in KWh (low).
d. Test on LED for tripping function.
e. Display of LED number.
f. Electronics faulty.
g. Power failure counter (Number of times power supply failed or disconnected)-400 cycles and back to Zero.
h. Enabling of disabled LED caused by tampering.
i. Number of days/hours into the current 30 days when there was power and total KWh used during the period
18. | EMC Compliance | Relevant section of IEC 62052-11:2020
19. | Burden | Preferably less than 2VA per phase
20. | Terminals | Extended cover type.
Hole diameter shall be a minimum of 9mm
21. | Casing/cover materials | Fire retardant – bakelite or polycarbonate
22. | Sealing | Provision must be adequate to prevent tampering
23. | Power Factor Range | -1 to +1
24. | Data Storage | Non –Volatile EPROM
25. | Switching | Latching contactor
26. | EMC Susceptibility | According to IEC 62052-11:2020, IEC 62053 – 22:2020, . Not adversely affected by external magnetic fields
27. | Life Span | Minimum 10 years
The meter shall decrement units for consumption in accordance with, and to the level of accuracy specified in the active tariff.