## Smart Tech Specs PPM
TECHNICAL SPECIFICATION FOR SMART 1-PHASE AND 3-PHASE METERS
S/No. | ITEM | AEDC REQUIREMENT | AEDC
1 | Nominal Voltage | - 1Ø-230V, 1-ph, 2-wire system, | Ok
|  | - 3Ø- 230/400V, 3-ph, 4-wire system (balanced and unbalanced load conditions) | Ok
2 | Operating Voltage | -40% to +10% Nominal Voltage | Ok
|  | -40% to +10% Nominal Voltage | Ok
3 | Current Rating | 5(100)A | 5(60)A
|  | 3 X5(100)A | 3 X5(100)A
4 | Frequency | 50 ±5%Hz | Ok
5 | Accuracy Class | Applicable IEC Standards as in Section 7.1.3 of the Nigerian Electricity Smart Metering Regulation 2015 | Class 1
6 | Encryption Algorithm for PPM | Standard Transfer Specification (STS) | Ok
7 | Operating Temp. | from -40°C to 70°C | Ok
8 | Storage Temp. | Up to 70°C | Ok
9 | Relative Humidity | 95% at 450C non- condensing | Ok
10. | Maximum KWH credit stored | 99,999.9 KWh(1Ø), 999,999.9KWh(3Ø) | Ok
11. | Credit transfer number | 20 Digits encryption | Ok
12. | Protection | High resistance to short circuit | Ok
13. | Impulse withstand voltage | Preferably greater than 6 KV | Ok
14. | Insulation withstand voltage | 2 KV per minute | Ok
15. | Name plate | a) Indelible Meter serial number shall not be more than twelve (12) digits and legibly printed | 13 Digits
|  | b) Size of the digit of the Meter serial number shall be a minimum of 5mm x 3mm. | Ok
|  | c) Bar code shall be printed below the Meter serial number | Ok
|  | d) Manufacturer’s name and Trademark. | Ok
|  | e) Place of manufacture. | Ok
|  | f) Year of manufacture. | Ok
|  | g) Reference Voltage, Current and frequency. | Ok
|  | h) Class index. | Ok
|  | i) Meter Constant. | Ok
|  | j) Owner/Utility’s Identity. | Ok
16. | Front panel Indication/Display | Include but not limited to the following:
|  | - Three level credit LED display | Ok
|  | o Green-when energy stored is full Yellow-when remaining credit will last for 3 days. | Ok
|  | o The red flashes when the remaining energy will last for 11/2 days. | Ok
|  | o Blue-Consumption rate indicator. LCD credit status display. | Ok
|  | - Credit transfer number accept/reject Tamper. | Ok
17. | Special Mode Display for Engineering / Management
Display up to 3 parameters according to programming to be specified:
|  | a. Normal display – LCD | OK
|  | i. Duplicate copy of token inserted | Ok
|  | ii. Credit Dispensing Unit identification number and KWh (or voucher serial number) inserted. | Ok
|  | iii. Electricity Dispenser (LED) full of units. | Ok
|  | iv. No power ON LED | Ok
|  | v. No credit on LED | Ok
|  | vi. Credit rejects or accepts. | Ok
|  | vii. Remaining Credit. | Ok
|  | viii. Instantaneous Power | Ok
|  | ix. Total KWh used in the past 24 hrs. | Ok
|  | x. Total KWh used in the past 30 days. | Ok
|  | xi. Total KWh used since the LED was installed. | Ok
b. Display only available with valid codes.
|  | c. Display only available within chosen programming or engineering mode. | Ok
|  | For the purpose of these specifications, items b) and c) above are treated as one. These shall be accessible only to utility staff. | Configuration software must and shall be provided, with Optical Port.
|  | a. Over current trip level. | Ok
|  | b. Green-Yellow Light emitting diode (LED) display change over level in KWh (high). | Ok
|  | c. Yellow-Red LED display change over level in KWh (low). | Ok
|  | d. Test on LED for tripping function. | Ok
|  | e. Display of LED number. | Ok
|  | f. Electronics faulty. | Ok
|  | g. Power failure counter (Number of times power supply failed or disconnected)-400 cycles and back to Zero. | Ok
|  | h. Enabling of disabled LED caused by tampering. | Ok
|  | i. Number of days/hour into the current 30 days when there was power and total KWh used during the period. | Ok
|  | Other | 6 months’ Historical kWh
|  | All PPM meters must be on AEDC SGC | OK
|  | Base Date 2014, meters only. (NO 2003 Base date meters) | OK
|  | Users interface unit. Wire or wireless | OK
|  | BS Meter Standard type P N N P for 1Ø | NO DIN Rail
|  | IEC Standard 6256-21 | OK
|  | Split type Key pad with UIU | OK
18. | EMC Compliance | Relevant section of IEC 61036. | OK
19. | Burden | Preferably less than 2 VA per phase. | OK
20. | Terminals | Extended cover type. Hole diameter shall be a minimum of 9mm. | OK
21. | Casing/Cover Material | Fire retardant-bakelite or polycarbonate | Ok
22. | Sealing | Provision must be adequate to prevent tampering. | Ok
23. | Power Factor Range | -1 to +1 | Ok
24. | Data Storage | Non-Volatile EPROM | Ok
25. | Switching | Latching contactor. | Ok
26. | EMC Susceptibility | According to IEC 61036, 61268.Not adversely affected by external magnetic fields. | Ok
27. | Life Span | Minimum 10 years | OK
28 | Meter type | 1Ø 1-ph with: - Two Internal CTs (one for line and Neutral) for measurement of current - Two Pole internal Breakers to isolate the supply completely - Goes into tamper mode when current in neutral is more than that in Line by 1 amp in a minute. | OK
29 | Measurement | 1Ø 1-ph, 2-wire system,3Ø 3- ph, 4 wire system and neutral current measurement | OK
30 | Disconnection relay | Maximum switching voltage: 400V Ac Maximum switching current: 120A Maximum switching power: 48kVA for 3 Phase and 16 kVA for 1-phase. | OK
31 | Battery | • Internal lithium battery: Easily replaceable battery without breaking seal. • Option for external for backup • Option for additional Supercap (72 hours) • Backup time: 10 years. | Easily replaceable battery without breaking seal.
32 | Environmental | • Specified operating range: -25ºC to +65ºC • Operating range limit: -40ºC to +80ºC • Storage range limit: -40ºC to +85ºC • Relative humidity: Up to 85% mean, 95% non-condensing for 30 days • Ingress protection: Transparent IP54 casing (Outdoor) | OK
Communication Specifications (Smart-features)
Meter will record activity in the memory with time and LED glow
1 | Communication interface | Optical as per IEC62056-21, supporting DLMS/COSEM protocol capable of transferring data | Ok
2 | Remote Communication interface | Meter Shall be able to communicate with Head end system through Gateway/Modem. Two way communication between meter and HES or via DCU through RF, PLC, LoRA and GPRS. DCU shall support TCP/IP, G3 PLC, Radio Frequency, Fibre, 3G or 4G. | Ok
3 | Midnight Energy Snapshot | Capable of recording and storing midnight snapshot of kWh, for minimum of 30 days and transferring same on demand and at predetermined interval. | Ok
4 | Interval data recording | 30 minutes with 3 voltages, current and power factors readings | OK
5 | Billing History | Current month + minimum last 6 months billing data | OK
6 | Event recording | Meter shall have facility to download using both optical port or via remote communication capability with date and time stamp. Following events to be recorded: | OK. VENDOR SHALL PROVIDE METER CONFIGURATION SOFTWARE, WITH UNLIMITED LICENCE
|  | As per tamper sheet a) Terminal Cover open (Tamper Led glow) | Ok
|  | b) Magnet Disturbance (Tamper Led glow) | Ok
|  | c) Phase Miss (R, Y, B) | Ok
|  | d) Current reverse (R, Y, B) | Ok
|  | e) Current Unbalance | Ok
|  | As per Event a) Power On/Off | Ok
|  | Status In Anomaly a) Over voltage (300.00Volts) | Ok
|  | b) Identification of neutral current more than line current | Ok
|  | c) Pre-programmed alarms for meter self-check | Ok
|  | d)Alarms trigger LEDs, enunciators, communications event | Ok
|  | e) Alarms are stored in event logs | Ok
7 | Remote connection-disconnection | Relay for remote load connection or disconnection with date and time stamp. Visual indication (Relay on/off) to be provided on display unit. | Ok
8 | Remote load control features | Feature to set threshold values to control load (over load Limit) of customers if demand is exceeded (Set by STS Token) | Ok
9 | Other remote functions | • Remote reading (Read by Modem) • Remote crediting (Set by STS Token with online transfer mechanism) • Acquire Meter profile/configuration data • Remote configuration of meters and DCUs. • Read meters according to pre-defined schedule or on-demand • Automatic re-reading of meters to acquire missed data • Remote disconnection/reconnection of energy supply • Upgrade meter firmware remotely | Ok
10 | Tariff Management | TOD billing and remote update to tariffs | OK
11 | Measured values | • Import/Export/Absolute: Wh, VArh and VAh • Per quadrant Wh, VArh and VAh • Power: W, VAr, VA, Vrms, Irms • 3 Power factors, 3 currents, 3 voltages frequency, phase sequence | OK
Backend Specifications
S/No. | Meter Type | Requirement | AEDC
1 | Single Phase PPM | 4G smart Communication Modem to AMI | GPRS 4Gfor stand-alone: meter
GPRS
2 | Single Phase Post Paid | Meter to Hand Held Unit (HHU), | RF
|  | HHU to HES to AMI | GPRS
3 | Three Phase PPM | 4G smart Communication Modem to AMI | GPRS for 4G smart energy meter. Standard EC600S-CN
|  | DCU to HES | GPRS
4 | Three Phase Post Paid | Meter to Hand Held Unit (HHU),
|  | HHU to HES to AMI | GPRS
5 | Whole Current | Meter to HES via GPRS (No DCU) | GPRS
6 | HES Architecture | Servers deployed in a multi-tiered environment | Okay
|  | • communication server | Okay
|  | • Application server | Okay
|  | • Database server deployed in a multi-tiered environment | Okay
• Meters and Data Concentrators should be connected to the HES via APNs
|  | • HES application server must be web-based, with a W3C-compliant web browser supporting HTTP and HTTPS over TCPIP | Okay
|  | • HES system must expose open interfaces for data exchange with Disco's Meter Data Management System (MDMS) | Okay
|  | Working on both hardware options i.e. 1. Meter to HES directly through 4 G GPRS 2. Meter to CIU through PLC, and then meter to HES system through GPRS | OPTION 1
7 | Data Concentrator Unit | Number (average of 100Mtrs to 1DCU) | No DCU
SPECIFICATION FOR USER INTERFACE UNIT (UIU)
S/N | FUNCTIONS AND FEATURES | AEDC TECHNICAL REQUIREMENTS | AEDC
1 | Operating Voltage | 230V AC, 6V DC | OK
2 | Operating Current | 10mA | OK
3 | Frequency | 50 ±2%Hz | OK
4 | Communication Mode | PLC,RF, MBus, e.t.c | Wireless, PLC RF
5 | Communication Distance | 100 meters minimum | OK
6 | Operating Temp. | Up to 60°C | OK
7 | Storage Temp. | Up to 70°C | OK
8 | Relative Humidity | 95% at 45° C non- condensing | OK
9 | Display | 1. LCD with good contrast and wide viewing angle with backlight features. | OK
2. Minimum of eight (8) digits representing the energy and at least one (1) digit after the first decimal point
3. LCD display size: 9mm x 4.5mm minimum
4. Viewing angle: 160 degrees minimum
5. Parameters:
i. Total units used to date (in KWh)
ii. Available credit (in KWh)
iii. Present consumption rate
iv. Last billing date
v. Last billed amount (KWh)
vi. Credit level
vii. Warning on credit level
viii. Other messages
10 | LEDs Display | 1. Green - Credit | OK
2. Yellow – Warning on no Credit
3. Red – No Credit
11 | Protection | IP54 | OK